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	Wiltshire Council Planning Consultation Response

	22nd May 2023
	Officer’s Name: Lynda King


	Wiltshire Council Drainage Engineer
Technical Services Drainage Engineer

Wiltshire Council 
	

	Application No:
	PL/2022/03103: Land to the East of Wagtails, Southampton Road, Alderbury, SP5 3AF

	Proposal:
	Outline Application for up to 30 dwellings (as amended) with all matters reserved (except access)


Please note the particulars in connection with the above planning application are available to view on the planning website http://www.wiltshire.gov.uk/planninganddevelopment.htm
Recommendations:

	
	No Comment

	
	Support

	X
	Support subject to conditions (please set out below)

	
	Object (for reasons set out below)

	
	No objections 


Matters Considered:

Documents Reviewed:

· Amended Site Plan 
· Application Form

· Letter from agent regarding outstanding issues

· Revised Access Details

· Revised Flood Risk Assessment

· Site Layout Plan

· Updated Drainage Correspondence 

· Wessex Water Plan 1&2
The application has been supported with a Site Specific Flood Risk Assessment (FRA). It should be noted that our comments below are reliant on the accuracy and completeness of the FRA and we do not take any responsibility for incorrect data or interpretation made by the authors.
Conditions:
The drainage team have the following conditions which need to be addressed by the applicant:
· The applicant shall demonstrate that minimum clearances (based on the density of the chalk) from soakaways to buildings / public highways are in accordance with CIRIA C574 and Wiltshire’s Soakaway Guidance

· The applicant should revise calculations for each of the following demonstrating:

· Soakaway calculations have applied a Factor of Safety of 10, rather than 2, as soakaway failure would culminate in widespread flooding on site. 
· The factor for urban creep has been applied in line with LASOO guidance.

· The Cv value should be 1 as the applicant is only considering the impermeable surfaces. Currently, the applicant has used Cv values of 0.75 (summer) and 0.84 (winter) considering the impermeable area only within their calculations (0.54ha).
· The applicant is required to submit calculations which demonstrate that the proposed drainage design provides a sufficient level of water treatment to prevent pollution of groundwater. 

· The applicant should submit clear arrangements for the ownership and ongoing maintenance of the proposed drainage system (including SuDS features).
· The applicant must provide a construction management plan which details how pollution to groundwater and local watercourses will be prevented while minimising flood risk to people and property. 
Informatives:
· The application states that foul drainage will discharge to a public sewer. This requires consultation with the sewerage undertaker for the area.
· LASOO urban creep calculation figures can be found here: https://www.susdrain.org/files/resources/other-guidance/lasoo_non_statutory_suds_technical_standards_guidance_2016_.pdf
--

Barney Taylor (Atkins working on behalf of Wiltshire Council Drainage).
