[image: image1.jpg]Wiltshire Council
e —————

oou—





	Wiltshire Council Planning Consultation Response

	31st May 2023
	Officer’s Name: Olivia Tresise


	Wiltshire Council Drainage Engineer
Technical Services Drainage Engineer

Wiltshire Council 
	

	Application No:
	PL/2023/03359 – Land West of Ashton Road, Ashton Keynes, Wilts, SN6 6QT

	Proposal:
	Construction and operation of anaerobic digestion facility, ancillary infrastructure and construction of new access from Ashton Road

	Site Address:
	

	Grid Ref:
	

	On Behalf of:
	


Please note the particulars in connection with the above planning application are available to view on the planning website http://www.wiltshire.gov.uk/planninganddevelopment.htm
Recommendations:

	
	No Comment

	
	Support

	
	Support subject to conditions (please set out below)

	X
	Object (for reasons set out below)

	
	No objections 


Matters Considered:

Documents Reviewed:

· Application Form
· Flood Risk Assessment

· Proposed Site Layout 

· Proposed Site Levels

· Site Context

· Site Elevation as Proposed

· Site Plan and 3D Images

“The application has been supported with a Site Specific Flood Risk Assessment (FRA). It should be noted that our comments below are reliant on the accuracy and completeness of the FRA and we do not take any responsibility for incorrect data or interpretation made by the authors.”
Objections:

The drainage team in their capacity as Lead Local Flood Authority have the below objections to the application; these must be overcome before a drainage objection can be removed:

1. The applicant should resubmit calculations to demonstrate a significant reduction in discharge rates. We acknowledge the applicant intends to restrict discharge rates to the greenfield rate, however Wiltshire Council requires 20% betterment to be achieved on greenfield rates for all storm events between the 1 in 1 year and the 1 in 100year return period storm events. To demonstrate this, the applicant must provide detailed drainage calculations for each of the 1 in 1, 1 in 30, and 1 in 100 year storm events. 
· Please refer to the informatives for clarification on greenfield calculations. 
Conditions:
The drainage team have the following conditions which need to be addressed by the applicant:
1. The applicant should provide drawings of the overland exceedance flows of the 1 in 100year plus climate change rainfall event that minimise the risk to people and property.
2. The applicant is required to submit calculations which demonstrate that the proposed drainage design provides a sufficient level of water treatment to prevent pollution of the receiving watercourse.
3. The applicant should provide information on whether the existing drainage ditches onsite will be maintained, utilised, or how they will be impacted post-development as shown in Figure 2-4 in the Flood Risk Assessment. 
4. The applicant must provide detailed cross sections and long sections drawings of the rainwater lagoon. 

5. The applicant must provide detailed cross sections and long sections drawings of the below ground propriety crate system. 

6. The applicant must provide a construction management plan which mitigates pollution to groundwater and adjacent watercourses, while mitigating flood risk to people and property.

7. The applicant should submit clear arrangements for the ownership and ongoing maintenance of the proposed drainage system (including SuDS features). 
Informatives:
· The applicant has calculated QBAR greenfield rates of 4.62l/s-1 but has instead selected to use a rate of 9.05l/s-1 (based on 2l/s/ha) as it provides a higher rate. This is not acceptable to the LLFA, and we would expect to see discharge limited in accordance with the betterment policy achieving 20% betterment on greenfield for all events between 1 in 1 and 1 in 100yearr. The applicant should revise their calculations based on this recommendation & demonstrate 20% betterment on greenfield discharge rates for all events between 1 in 1 and 1 in 100year. 
· Wiltshire Council is the land drainage authority under the Land Drainage Act 1991. Land drainage consent is required if a development proposes to discharge flow into an ordinary watercourse or carry out work within 8m of an ordinary watercourse. 

· An ordinary watercourse is a watercourse that does not form part of a main river. The term watercourse includes all rivers and streams and all ditches, drains, cuts, culverts, dikes, sluices, sewers (other than public sewers within the meaning of the Water Industry Act 1991) and passages, through which water flows.

· The land drainage consent application form and guidance notes can be found on our website here: https://www.wiltshire.gov.uk/civil-emergencies-land-drainage-ordinary-watercourse
Barney Taylor (Atkins working on behalf of Wiltshire Council Drainage).
