Dear Peter Crozier, 
Re: PL/2025/07726, Electric vehicle charging facility. Land North of Bath Road, Chippenham, SN14 0BJ. 
We have reviewed the above planning application and have the following comments to make. 
Background

This planning application is for 16 rapid EV charging units Battery storage compound Lighting and CCTV Substation Feeder pillar Signage
Noise 
We have reviewed the noise impact assessment reference – 11627/CP submitted on 25th September 2025 by Acoustic Consultant LTD. 
The nearest residential dwelling is approximately 20meters from the proposed development. 
Figure 2: Site layout drawing refers to a proposed acoustic fence between the development and the nursery; however, no mitigation has been proposed in the noise impact assessment – Please can details be submitted. 
Section 5 Noise monitoring
5.3. Please can justification for the monitoring location be submitted. The location chosen appears to be in a wooded section covered with vegetation which could impact the results
Section 6 Proposed EV Charging plant 
6.1 It is proposed that the plant will be located east of the existing nursery with 12no. 160kW single arm DC chargers and 4no. 160kW double arm DC chargers. Both assumed to produce the same noise levels with no tonality, or character corrections. 

The BS4142 estimate shown in section 8.4 shows that the daytime levels will achieve our standard of -5dB, however nighttime levels will be +1dB. We expect that new plant will achieve our standard of -5dB as much as possible. 

We are concerned that the noise impact from cars entering the development has not been included in the noise impact assessment. This development is brining cars closer to residential dwellings and no consideration has been made. 
We also note that the battery storage compound has not been included in the noise impact assessment. We would expect to see the impact of the fans and heating and cooling systems as these have become a growing concern, especially when build in close proximity to residential areas. 
We recommend the applicant reviews our noise and technical guidance which provides information on good acoustic design and the hierarchy of noise. Wiltshire_Council_Noise_and_Planning_Technical_Guidance_V.1.pdf
Further advice can be found by visiting this link: 
Environmental advice for developers and planning agents - Wiltshire Council
Contamination 
We have reviewed the Phase 1 Land contamination risk assessment reference 4084D P1 HAND Chippenham. 
Contamination is not expected to exist on the site, and we cannot see any flags on our mapping system. However, I feel it is appropriate to add a condition as the risk levels to sensitive receptors such as the daycare nursery is low to moderate. 
Therefore, I recommend the following 

In the event that contamination is found at any time when carrying out the approved development, the Local Planning Authority shall be notified immediately. Development shall cease in the affected area and a written method statement detailing the nature of the contamination and the proposed remediation measures shall be submitted to and approved in writing by the Local Planning Authority. The remediation measures shall be carried out in accordance with the approved details. Following completion of the remediation, a verification report confirming that the site is suitable for its permitted use shall be submitted to and approved in writing by the Local Planning Authority before development recommences in the affected area. 
  Reason:  
 To ensure compliance with Core Policy 56 and to reduce the risks associated with land contamination 
Construction 
Due to the close proximity of residential dwellings, we require a CEMP. We recommend the following condition 
The development hereby approved shall not commence until a Construction and Environmental Management Plan (CEMP) has been submitted to and approved in writing by the local planning authority. The CEMP shall include details of the following relevant measures:  
i. An introduction consisting of construction phase environmental management plan, definitions and abbreviations and project description and location;  
ii. A description of management responsibilities;  
iii. A description of the construction programme;  
iv. Site working hours and a named person for residents to contact;  
v. Detailed Site logistics arrangements;  
vi. Details regarding parking, deliveries, and storage;  
vii. Details regarding dust and noise mitigation;  
viii. Details of the hours of works and other measures to mitigate the impact of construction on the amenity of the area and safety of the highway network; and  
ix. Communication procedures with the LPA and local community regarding key construction issues – newsletters, fliers etc.  
There shall be no burning undertaken on site at any time. 
Construction hours shall be limited to 0800 to 1800 hrs Monday to Friday, 0800 to 1300 hrs Saturday and no working on Sundays or Bank Holidays.  
 Reason: Core policy 57, Ensuring high design and place shaping such that appropriate levels of amenity are achievable. 

Based on the following I must recommend refusal of this application until the additional information has been submitted.
Kind regards Public Protection

