FLOOD RISK ASSESSMENT March 2026 (written with sight of Wiltshire’s Level 1 Strategic Flood Risk Assessment Nov 2024)

Site: 
Dairy Cottage, North Newnton, Pewsey, Wiltshire SN9 6LA

Proposed Development: 
The replacement of an existing non-mains sewerage system with a small sewage treatment plant (STP), including the installation of associated pipes, cables, vents, ducts, manholes or kiosks, and alongside ancillary engineering operations. Existing surface treatments will be reinstated following works.

Flood Risk: 
The proposed development lies within flood zone 2/3 where the principal flood risk is from a tributary of the River Avon. This small watercourse runs to the west beyond the site boundary, approximately 35m away from the nearest proposed groundworks. The River Avon (a main river) runs approximately 120m east of the site, but the distance between is not marked as flood zone.

The EA’s long term flood risk service (Where do you want to check? - Check your long term flood risk - GOV.UK)shows this address as having the following flood risks:

| Risk of yearly river flooding | Risk of yearly river flooding 2036-2069 | Risk of yearly surface water flooding | Risk of yearly surface water flooding 2040-2060 | Risk of groundwater flooding | Risk of flooding from reservoirs |
| --- | --- | --- | --- | --- | --- |
| Very low | Low | Very low | Very low | Inside a groundwater flood alert area | There is a risk |

Risk from Defence Overtopping
The STP will be at permanent risk of flooding as a result of any offsite defences overtopping, as the installation is underground and there are no known defences in place between the river and the new STP. Chances of flooding modelled by the Environment Agency are shown in the table below.

| Annual likelihood of surface water flooding | Less than 1 in 1000 |
| --- | --- |
| Flood zones 2 and 3 2070 to 2125 | Extends further across the property |

Finished Levels
The STP will be at permanent risk of flooding as installation is underground and within the risks suggested in this report.

Flood Resistance & Resilience
The STP products are designed to avoid failure through flooding. Combined with appropriate project design and installation on site, the STP should meet the following criteria:

- The blower / electronics are above flood level

- Units are fitted with a pumped outlet to ensure continued operation when outlet is under water. The units have a non-return valve built in, allowing the unit to discharge when the outlet is below water.

- The lid will be above the flood level, fitted with a sealed cover to further mitigate risk.

- Sealed covers are fitted to any part of the drainage system to prevent surface water entry.

- The unit will be encased in concrete to prevent floatation.

Supporting Plans and drawings
Drawings of the proposed STP installation have already been provided to the Wiltshire Planning Department as part of the overall planning application. The EA’s flood map is shown below.