Fire Statement for the proposed development at 
Boreham Mill Bishopstrow, Warminster BA12 9HQ.

This fire statement outlines the fire safety strategy for a proposed residential building comprising a ground floor and three upper storeys (six flats total). It is designed to demonstrate compliance with Building Regulations 2010 and Fire Safety (England) Regulations 2022.
1. Building Overview
· Structure: Ground floor plus three upper floors.
· Occupancy:
· Ground Floor: 2 flats.
· First Floor: 2 flats.
· Second Floor: 1 flat.
· Third Floor: 1 flat.
· Total Dwellings: 6 self-contained residential units.
2. Means of Escape Strategy
The primary strategy is based on an all out evacuation policy with benefit  that all  the occupants remain safe due to high levels of compartmentation.
· Primary Route: Internal protected main staircase serving all floors, leading to a final exit at ground level.
· Secondary Route: An existing external fire escape provides an alternative means of escape from every floor level, ensuring residents have a secondary path to a place of ultimate safety if the internal stairs become compromised.
· Fire Doors: All flat entrance doors are self-closing FD30S fire doors, providing 30 minutes of fire and smoke resistance.
3. Compartmentation and Fire Spread
· Fire Separation: Every flat is a fire-resisting "box." Floors and internal walls between flats provide a minimum of 60 minutes of fire resistance to prevent vertical and horizontal fire spread.
· External Walls: The external wall system is check  that it is not constructed of any combustible  materials and if   the material are found to be combustible, the material will be removed to prevent fire spread across the building's face. This applies to the first floor extension on the southern elevation
4. Fire Detection and Alarm Systems
· Domestic Detection: Each flat is equipped with a Grade D1/D2 LD2 smoke alarm system (interlinked mains-powered alarms with battery backup) in accordance with BS 5839-6.
· Communal Areas: A manual or automatic fire detection system may be installed in the communal staircase to actuate smoke ventilation or alert the Fire and Rescue Service (FRS).
5. Fire Service Access and Facilities
· Access: Fire appliances can gain unobstructed access to the building's main entrance.
· Water Supply: The River Wylie  provides a significant on site supply of water A hydrant or suitable water source is located within the required distance from the building's perimeter.
· Signage: Clear wayfinding signage and fire exit markings are provided throughout communal areas and the external fire escape.
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