Wiltshire Council Planning Consultation Response

ECOLOGY

| Officer name: | Patrick Olshansky |  |
| --- | --- | --- |
| Date: | 21/04/2026 02/06/2026 |  |
| Application No.: | PL/2026/02007 & PL/2026/02008 |  |
| Proposal: | Partial discharge of Condition 15 (External Lighting) and Condition 16 (Hard and Soft Landscaping) relating to application PL/2024/09312 - south parterre & sunken south lawn |  |
| Site Address: | Tottenham House and Estate, Grand Avenue, -, Savernake, SN8 3BE |  |
| Case Officer: | Helen Garside |  |

| Condition No. | Further information required by condition | Satisfactorily addressed (Document & Date) |
| --- | --- | --- |
| PL/2026/02007 - Partial discharge of Condition 15 (External Lighting) and Condition 16 (Hard and Soft Landscaping) relating to application PL/2024/09312 - south parterre |  |  |
| 15 | No external lighting shall be installed on any building and/or other relevant area of the Estate or part thereof until plans showing the type of light appliance, the height and position of fitting, illumination levels and light spillage in accordance with the appropriate Environmental Zone standards set out by the Institute of Lighting Engineers in their publication " Institution of Lighting Professionals (ILP), Guidance Notes for the Reduction of Obtrusive Light, GN01:2021", have been submitted to and approved in writing by the Local Planning Authority for the relevant building and/or area of the Estate or part thereof. REASON: In the interests of the amenities of the area and to minimise unnecessary light spillage above and outside the development site. INFORMATIVE TO APPLICANT: The lighting scheme must avoid any light spill in areas of woodland and/or other areas where there are known wildlife interests, such as bat commuting corridors. | Minor clarification required. See comments below. YES (02/06/2026) - Covering Letter, prepared by Newmark - Condition Statement (ref. GSS/6150 Rev. 03), prepared by - ADAM Architecture - Light Calculation Report, prepared by DIALux - Lighting Equipment Specification (ref. L10751A-LES-01 Rev. 07), dated 05.03.2026, prepared by DPA Lighting Consultants - Landscape Lighting Layout Sheet 7 of 8, East Gardens, North - and South Terrace (ref. L10751A_LP_LS_07 Rev. 08), - prepared by DPA Lighting Consultants - Lighting Control Schedule (Rev. 05), dated 20.02.2026, prepared DPA Lighting Consultants - Tottenham House Bat Corridor Light Calculation Report South Parterre 19/05/2026 |
| PL/2026/02008 - Partial discharge of Condition 15 (External Lighting) and 16 (Hard and Soft Landscaping) of PL/2024/09312 - sunken south lawn |  |  |
| 15 | No external lighting shall be installed on any building and/or other relevant area of the Estate or part thereof until plans showing the type of light appliance, the height and position of fitting, illumination levels and light spillage in accordance with the appropriate Environmental Zone standards set out by the Institute of Lighting Engineers in their publication " Institution of Lighting Professionals (ILP), Guidance Notes for the Reduction of Obtrusive Light, GN01:2021", have been submitted to and approved in writing by the Local Planning Authority for the relevant building and/or area of the Estate or part thereof. REASON: In the interests of the amenities of the area and to minimise unnecessary light spillage above and outside the development site. INFORMATIVE TO APPLICANT: The lighting scheme must avoid any light spill in areas of woodland and/or other areas where there are known wildlife interests, such as bat commuting corridors. | Minor clarification required. See comments below. YES (02/06/2026) - Covering Letter, prepared by Newmark - Condition Statement (ref. GSS.6150 Rev. A), prepared by ADAM Architecture - Sunken Lawn Lighting Equipment Specification - ref. L10751A LES-SL-R00 Rev. 00 (dated 13 March 2026), prepared by DPA Lighting Consultants - Bat Corridor Light Calculation Report - Sunken Lawn Stairs no. Rev (dated 5 March 2026), prepared by DPA Lighting Consultants - Landscape Lighting Layout Sheet 9 of 9 Sunken Lawn (ref. L10751A-LP-LS-09 Rev.00), prepared by DPA Lighting Consultants - Lighting Control Schedule (Rev. 05), dated 20.02.2026, prepared DPA Lighting Consultants |

Condition 15

Permission 17/12461/OUT (07 Dec 2018) includes Condition 16 controlling lighting; an ecology informative advises avoiding light spill into woodland and known wildlife areas (e.g., bat corridors). Condition 16 has been partially discharged for subsections via approved lighting schemes for the main house (PL/2025/01369), stable block (PL/2024/09311) and several infrared CCTV installations (PL/2024/07155; PL/2022/01569; PL/2021/07513). PL/2024/09312 (variation) contains Condition 15, worded similarly to Condition 16 and accompanied by the same ecology informative.

PL/2026/02007 and PL/2026/02008 seek partial discharge of Condition 15 for landscaping immediately south of the main house (south parterre and sunken lawn). Condition 15 cites ILP GN01:2021 (landscape/amenity lighting focus) and it is unclear whether the ecology informative is enforceable; if it is not, no ecology response may be required.

The 2017 Ecological Assessment for parent application is outdated but recommended low‑level lighting and limiting light spill, as did the Ecology planning response which recommended a maximum of ≤ 0.5 lux at surrounding tree/shrub lines to protect foraging/commuting bats.

205 LED luminaires are proposed and the layouts/specs generally meet the condition. However, the light calculations are shown on blank backgrounds and lack site context; they appear to be part of a wider Tottenham House Bat Corridor report. Please submit the full Bat Corridor report or amended plans/clarification showing the calculation surfaces overlaid on the site layout and adjacent habitats so illumination and light spill can be properly assessed. An updated calculation report (see above) has been submitted and shows the horizontal and vertical illuminance from the south parterre. Illumination levels are below 0.02 along the roadway to the south which is acceptable.

Note to case officer: DoC PL/2025/01369 (main house façade lighting) was approved before VAR PL/2024/09312; a proposed picture‑gallery extension to main house not covered by the earlier scheme may therefore require reassessment of lighting scheme.

Condition 16

Partial discharges of landscaping condition 16 being sought under PL/2026/02007 and PL/2026/02008. This is a landscape setting related condition and it is not believed that ecology are required to comment.

Final sign off – all matters addressed:

| Ecologist: Patrick Olshansky | Date: 02/06/2026 |
| --- | --- |