FLOOD RISK ASSESSMENT Aug 2026 (written with sight of Wiltshire’s Level 1 Strategic Flood Risk Assessment Nov 2024)
Site: 
FROG LANE BARN, 86 SAND STREET, LONGBRIDGE-DEVERILL, WARMINSTER BA12 7DS
Proposed Development: 
The replacement of an existing non-mains sewerage system with a small sewage treatment plant (STP), including the installation of associated pipes, cables, vents, ducts, manholes or kiosks, and alongside ancillary engineering operations. Existing surface treatments will be reinstated following works.
Flood Risk: 
The proposed development lies within flood zone 2 and 3 where the principal flood risk is from the River Wylye, which flows along the southern boundary of the applicant’s property. The proposed development lies within 30 meters from this river. 
The EA’s long term flood risk service (Where do you want to check? - Check your long term flood risk - GOV.UK)shows this address as having the following flood risks:
	Risk of yearly river flooding
	Risk of yearly river flooding 2036-2069
	Risk of yearly surface water flooding
	Risk of yearly surface water flooding 2040-2060
	Risk of groundwater flooding
	Risk of flooding from reservoirs

	Very low
	Very low 
	Very low
	Very low
	Unlikely
	Unlikely



Risk from Defence Overtopping
The STP will be at permanent risk of flooding as a result of any offsite defences overtopping, as the installation is underground and there are no known defences in place between the river and the new STP. Chances of flooding modelled by the Environment Agency are shown in the table below.
	
	

	Annual likelihood of surface water flooding
	Less than 1 in 1000

	Flood zones 2 and 3 2070 to 2125
	Extends further into the property



Finished Levels
The STP will be at permanent risk of flooding as installation is underground and within the risks suggested in this report.
Flood Resistance & Resilience
The STP products are designed to avoid failure through flooding. Combined with appropriate project design and installation on site, the STP should meet the following criteria:
· The blower / electronics are above flood level
· Units are fitted with a pumped outlet to ensure continued operation when outlet is under water. The units have a non-return valve built in, allowing the unit to discharge when the outlet is below water.
· The lid will be above the flood level, fitted with a sealed cover to further mitigate risk.
· Sealed covers are fitted to any part of the drainage system to prevent surface water entry.
· The unit will be encased in concrete to prevent floatation.
Supporting Plans and drawings
Drawings of the proposed STP installation have already been provided to the Wiltshire Planning Department as part of the overall planning application. The EA’s flood map is shown below.
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