# Solar Installation Technical Information

Land East of Cadley Farmhouse  Chute Cadley  Andover  SP11 9EB

Purpose. This statement summarises the principal technical specifications of the proposed ground-mounted photovoltaic array and the associated inverter and battery equipment. It should be read with the submitted site layout, elevations and supporting planning statements.

# System Overview

| Item | Specification |
| --- | --- |
| Generating capacity | 14.64 kWp photovoltaic array |
| Panel arrangement | 24 panels arranged in three banks of eight, mounted in portrait orientation |
| Panel orientation | Installer schedule records an orientation 45 degrees from south (azimuth 136 degrees) and a fixed inclination of 20 degrees from horizontal |
| Estimated annual output | Approximately 13,791 kWh, based on the installer's MCS calculation |
| Inverter capacity | 10 kW single-phase energy controller |
| Battery storage | 16.12 kWh total nominal capacity; approximately 15.6 kWh usable capacity |
| Grid connection | SSEN G99 connection arrangement; export limited to 4 kW |

# Solar Panels

| Item | Specification |
| --- | --- |
| Manufacturer and model | JA Solar JAM66D45-610/LB DeepBlue 4.0 Pro |
| Quantity and rating | 24 modules at 610 W each |
| Construction | High-efficiency n-type monocrystalline bifacial, double-glass module |
| Module dimensions | 2,384 mm high x 1,134 mm wide x 30 mm deep |
| Module weight | 33.7 kg each |
| Module efficiency | 22.6% at standard test conditions |
| Glass and frame | 2.0 mm front glass and 2.0 mm rear glass with aluminium frame |
| Junction box | IP68 rated |
| Operating range | -40 degrees C to +85 degrees C |
| Design loading | Maximum static load: 5,400 Pa front and 2,400 Pa rear |
| Warranty | 12-year product warranty and 30-year linear performance warranty |

# Mounting Structure and Array Envelope

| Item | Specification |
| --- | --- |
| Mounting system | SolarPort galvanised-steel posts and cross-rails |
| Ground fixing | Posts driven directly into the ground without concrete foundations |
| Overall envelope | Approximately 9.1 m x 15.25 m |
| Maximum height | Approximately 1.65 m above existing ground level |
| Inclination | Fixed at approximately 20 degrees from horizontal |
| Reversibility | The mounting system can be removed and the ground reinstated when no longer required |

# Inverter and Battery Storage

| Item | Specification |
| --- | --- |
| Energy controller | 1 x Sigenergy SigenStor EC 10.0SP, single phase, rated at 10 kW |
| Battery modules | 2 x Sigenergy SigenStor BAT 8.0 lithium iron phosphate battery modules |
| Battery capacity | 8.06 kWh nominal and 7.8 kWh usable per module; 16.12 kWh nominal and approximately 15.6 kWh usable in total |
| Equipment envelope | The combined two-module SigenStor equipment stack is approximately 850 mm wide x 260 mm deep x 910 mm high |
| Weight | Approximately 183 kg for the combined two-module equipment stack |
| Cooling | Natural convection; no mechanical cooling plant is specified |
| Ingress protection | IP66 rated equipment |
| Safety and standards | LiFePO4 battery chemistry with multi-layer protection. Manufacturer documentation records compliance with applicable IEC/EN electrical and battery safety standards |
| Warranty | 10-year manufacturer product warranty for the controller and batteries |

# Location Within the Field Store

The inverter and battery equipment will be housed internally within the previously approved field store. The equipment will occupy less than 1 m² of its 25.7 m² floor area, leaving more than 96% of the building available for its principal agricultural storage use. The equipment will not require any alteration to the approved external form or appearance of the building.

Internal accommodation protects the equipment, avoids external visual clutter and removes the need for a separate cabinet or ancillary structure beside the array. Cabling between the array and field store will be installed underground.

# Operational Characteristics

The array is fixed and contains no tracking mechanism. No external lighting, concrete foundations or external equipment enclosure is proposed. The battery system and energy controller use natural convection cooling, with no externally mounted mechanical cooling plant.

Source: Solar Searcher Ltd proposal for Cadley Farmhouse and the accompanying JA Solar and Sigenergy technical sheets. Array dimensions and mounting details are taken from the submitted planning drawings and Design and Access Statement.